SECTION 22 34 13

Instantaneous, Tankless, Gas Domestic Water Heaters

[Specifier Notes] – This document uses hidden text to guide the specifier through various options while editing the document.  Hidden text may be turned on by quickly by clicking on the “Show/Hide” symbol “¶” in the ribbon; by going to “File” above the ribbon at the top left, then to “Options” at the very lower left, then to “Display” on the left side of the menu pop-up, and then check the box next to “Hidden Text.”

Please delete this note before printing.

- General

SUMMARY

Section Includes:

Indoor Tankless Gas Water Heaters.

Outdoor Tankless Gas Water Heaters.

Indoor or Outdoor Tankless Rack Systems.

Definitions

Tankless Gas Domestic Water Heater: Internally or externally mounted, or freestanding, commercial condensing, multiple point-of-use, gas fired water heater.

Submittals

Submit in accordance with requirements of Section 01 30 00 - Administrative Requirements.

Product Data: Manufacturer's technical data sheets, specifications, performance data and installation instructions for all products referenced in the scope of work defined in this section.

Shop Drawings: Submit shop drawings required to depict the requirements for fabrication and installation. Include the following drawings as applicable:

Include dimension drawings of water heaters indicating components and connections to other equipment and piping.

Include heat-exchanger dimensions, size of tappings, and performance data.

Closeout Submittals

Provide original manufacturer’s installation and operation manuals.

Provide written manufacturer’s warranty.

Quality Assurance

Manufacturer Qualifications: Primary products in this section to be provided by a manufacturer with no less than five years of experience producing the products specified in this section at a facility in the United States.

Installer's Qualifications: All work specified in this section is to be completed by a firm with demonstrated experience installing systems similar in scope and complexity to those specified.

Delivery, Storage and Handling

Deliver, store and handle materials and products in accordance with the manufacturer's instructions and recommendations and industry standards.

Store all materials in the manufacturer’s original packaging until ready for installation. Protect all products from damage or exposure to adverse environmental conditions, including weather, humidity, and dust.

Provide temporary inlet and outlet caps, maintain caps in place until installation.

Project Conditions

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

Warranty

Manufacturer’s Warranty: Manufacturer agrees to replace products that fail within the specified warranty period.

Failure Methods: Condensate corrosion, thermal stress, mechanical defects, or workmanship.

Heat Exchanger: 15 years from date of Substantial Completion under standard or controlled regulation.

All Other Parts and Components: 5 years from date of Substantial completion.

Products

MANUFACTURERS

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Manufacturer: Navien Inc.

20 Goodyear, Irvine, CA 92618.

Website: www.navieninc.com.

Phone: (800) 519-8794.

[Specifier Notes] – Retain the following Paragraph if this document is written as a PERFORMANCE specification, without listing a manufacturer as a basis of design. Insert manufacturers that sell products comparable to those specified in this section. Delete if not required.

Provide products by one of the following manufacturers subject to compliance with the requirements below:

Navien Inc.

Or Equal.

Substitution Limitations:

Submit substitution requests in accordance with provisions of Section 01 60 00.

Single manufacturer to provide, from a single source, primary products and accessories specified in this section.

PERFORMANCE REQUIREMENTS

Certifications: Provide products with heat exchanger that has the following certification labels.

ANSI and CSA marks for the United States and Canada.

AHRI certification for the United States and Canada.

[Specifier Notes] – Controller Design UL File Number: E146595.

UL certification controller for recovery and external recirculation marks for the United States and Canada.

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by an NRTL, and marked for intended location and use.

ASHRAE/IES Compliance: Fabricate and label fuel-fired, domestic-water heaters to comply with ASHRAE/IES 90.1.

Comply with efficiency requirements in ASHRAE 189.1, which supersede requirements in ASHRAE/IESNA 90.1.

NSF Compliance: Fabricate and label equipment components that will be in contact with potable water to comply with NSF 61 and NSF 372.

Energy Star Compliance: Fabricate and label equipment in compliance with Energy Star requirements.

Specifier Note - Retain the following subparagraph if domestic-water heater is required for foodservice equipment.

      - Special Requirements: NSF 5 construction.

High Altitude: approved up to 10,200 ft or (3,109 m).

SCAQMD Rule 1146.2 Type 1 Compliance: Provide units with low nitrous oxide emissions that meet or exceed 14 ng/j or 20 ppm NOx requirements at 3%.

System Requirements

General: Provide tankless condensing water heater with microprocessor control and a direct electronic ignition system (with no standing pilot), fully modulating gas control valve, turbine flow meter, automatic electro-mechanical water flow control valve, and water temperature thermistors to maintain outlet water temperature between ± 2°F of set point temperature. Microprocessor shall have built in recirculation logic to control a pump’s heating cycles.

Controls: Provide an integrated temperature thermostat with an adjustable set point range of 96°F to 185°F.

Error Memory: Provide water heater with no less than nine diagnostic maintenance codes that can be read via the display on the temperature thermostat controller.

Emissions: Provide water heater that produces no more than 20 ppm NOx emissions when tested in accordance with the rules and regulations of the South Coast Air Quality Management District.

Burners: Provide tankless water heater with downward fired fiber mesh burners, solid brass water flow control valve, and solid brass inlet and outlet water connections.

Junction Box: Provide pre-installed electrical junction box.

Heat Exchanger Construction: 400 series stainless steel.

Indoor Tankless Gas Water Heaters.

General: ANSI Z21.10.3/CSA 4.3 for gas-fired, hybrid, domestic-water heaters for indoor application.

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Product: Navien NPE, Model 150S2.

Uniform Energy Factor: 0.93.

Temperature Setting Range: 97 to 185 degrees F (36 to 85 degrees C).

Fuel: Natural Gas or Propane.

Gas Consumption: 18,000 to 120,000 Btu/hr.

Gas Supply Pressure:

Natural Gas: 3.5 to 10.5 inches of water column.

Propane: 8.0 to 13.5 inches of water column.

Electrical: Provide 120 V/60 Hz AC power source, with consumption as follows:

Normal Usage: 52 Watts.

Max Current: 4 Amps.

Hot Water Flow Rate Capacity: 6.8 GPM at 35°F temperature rise.

Pressure Rating: 150 psi

Heat Exchanger: Dual, stainless steel heat exchangers.

Freeze Protection: For ambient temperatures as low as –5°F.

General: ANSI Z21.10.3/CSA 4.3 for gas-fired, hybrid, domestic-water heaters for indoor application.

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Product: Navien NPE, Model 180S2.

Uniform Energy Factor: 0.96.

Temperature Setting Range: 97 to 185 degrees F (36 to 85 degrees C).

Fuel: Natural Gas or Propane.

Gas Consumption: 10,000 to 150,000 Btu/hr.

Gas Supply Pressure:

Natural Gas: 3.5 to 10.5 inches of water column.

Propane: 8.0 to 13.5 inches of water column.

Electrical: Provide 120 V/60 Hz AC power source, with consumption as follows:

Normal Usage: 52 Watts.

Max Current: 4 Amps.

Hot Water Flow Rate Capacity: 8.4 GPM at 35°F temperature rise.

Pressure Rating: 150 psi

Heat Exchanger: Dual, stainless steel heat exchangers.

Freeze Protection: For ambient temperatures as low as –5°F.

General: ANSI Z21.10.3/CSA 4.3 for gas-fired, hybrid, domestic-water heaters for indoor application.

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Product: Navien NPE, Model 180A2.

Uniform Energy Factor: 0.95.

Temperature Setting Range: 97 to 185 degrees F (36 to 85 degrees C).

Fuel: Natural Gas or Propane.

Gas Consumption: 10,000 to 150,000 Btu/hr.

Gas Supply Pressure:

Natural Gas: 3.5 to 10.5 inches of water column.

Propane: 8.0 to 13.5 inches of water column.

Electrical: Provide 120 V/60 Hz AC power source, with consumption as follows:

Normal Usage: 52 Watts.

Max Current: 4 Amps.

Hot Water Flow Rate Capacity: 8.4 GPM at 35°F temperature rise.

Pressure Rating: 150 psi

Heat Exchanger: Dual, stainless steel heat exchangers.

Freeze Protection: For ambient temperatures as low as –5°F.

Recirculation Pump: Internal recirculation pump to provide a zero GPM activation rate.

Buffer Tank: Provide Internal insulated 0.5-gallon buffer tank to eliminate the introduction of cold water into the hot water supply line on occasions of frequent on/off operations.

General: ANSI Z21.10.3/CSA 4.3 for gas-fired, hybrid, domestic-water heaters for indoor application.

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Product: Navien NPE, Model 210S2.

Uniform Energy Factor: 0.96.

Temperature Setting Range: 97 to 185 degrees F (36 to 85 degrees C).

Fuel: Natural Gas or Propane.

Gas Consumption: 12,000 to 180,000 Btu/hr.

Gas Supply Pressure:

Natural Gas: 3.5 to 10.5 inches of water column.

Propane: 8.0 to 13.5 inches of water column.

Electrical: Provide 120 V/60 Hz AC power source, with consumption as follows:

Normal Usage: 52 Watts.

Max Current: 4 Amps.

Hot Water Flow Rate Capacity: 10.1 GPM at 35°F temperature rise.

Pressure Rating: 150 psi

Heat Exchanger: Dual, stainless steel heat exchangers.

Freeze Protection: For ambient temperatures as low as –5°F.

General: ANSI Z21.10.3/CSA 4.3 for gas-fired, hybrid, domestic-water heaters for indoor application.

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Product: Navien NPE, Model 210A2.

Uniform Energy Factor: 0.95.

Temperature Setting Range: 97 to 185 degrees F (36 to 85 degrees C).

Fuel: Natural Gas or Propane.

Gas Consumption: 12,000 to 180,000 Btu/hr.

Gas Supply Pressure:

Natural Gas: 3.5 to 10.5 inches of water column.

Propane: 8.0 to 13.5 inches of water column.

Electrical: Provide 120 V/60 Hz AC power source, with consumption as follows:

Normal Usage: 52 Watts.

Max Current: 4 Amps.

Hot Water Flow Rate Capacity: 10.1 GPM at 35°F temperature rise.

Pressure Rating: 150 psi

Heat Exchanger: Dual, stainless steel heat exchangers.

Freeze Protection: For ambient temperatures as low as –5°F.

Recirculation Pump: Internal recirculation pump to provide a zero GPM activation rate.

Buffer Tank: Provide Internal insulated 0.5-gallon buffer tank to eliminate the introduction of cold water into the hot water supply line on occasions of frequent on/off operations.

General: ANSI Z21.10.3/CSA 4.3 for gas-fired, hybrid, domestic-water heaters for indoor application.

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Product: Navien NPE, Model 240S2.

Uniform Energy Factor: 0.96.

Temperature Setting Range: 97 to 185 degrees F (36 to 85 degrees C).

Fuel: Natural Gas or Propane.

Gas Consumption: 13,300 to 199,900 Btu/hr.

Gas Supply Pressure:

Natural Gas: 3.5 to 10.5 inches of water column.

Propane: 8.0 to 13.5 inches of water column.

Electrical: Provide 120 V/60 Hz AC power source, with consumption as follows:

Normal Usage: 52 Watts.

Max Current: 4 Amps.

Hot Water Flow Rate Capacity: 11.2 GPM at 35°F temperature rise.

Pressure Rating: 150 psi

Heat Exchanger: Dual, stainless steel heat exchangers.

Freeze Protection: For ambient temperatures as low as –5°F.

General: ANSI Z21.10.3/CSA 4.3 for gas-fired, hybrid, domestic-water heaters for indoor application.

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Navien’s products listed as the Basis of Design. Delete if not required.

Basis of Design Product: Navien NPE, Model 240A2.

Uniform Energy Factor: 0.95.

Temperature Setting Range: 97 to 185 degrees F (36 to 85 degrees C).

Fuel: Natural Gas or Propane.

Gas Consumption: 13,300 to 199,900 Btu/hr.

Gas Supply Pressure:

Natural Gas: 3.5 to 10.5 inches of water column.

Propane: 8.0 to 13.5 inches of water column.

Electrical: Provide 120 V/60 Hz AC power source, with consumption as follows:

Normal Usage: 52 Watts.

Max Current: 4 Amps.

Hot Water Flow Rate Capacity: 11.2 GPM at 35°F temperature rise.

Pressure Rating: 150 psi

Heat Exchanger: Dual, stainless steel heat exchangers.

Freeze Protection: For ambient temperatures as low as –5°F.

Recirculation Pump: Internal recirculation pump to provide a zero GPM activation rate.

Buffer Tank: Provide Internal insulated 0.5-gallon buffer tank to eliminate the introduction of cold water into the hot water supply line on occasions of frequent on/off operations.

Tankless Rack Systems

Tankless Free-Standing Rack System – Base Kit.

Capacity: Single unit, front mounted or Two unit, mounted Back to back.

Rack Frame: 1.5 inch square tube 14 gauge hot rolled steel.

Tankless Free-Standing Rack System – Add-on Kit.

Capacity: Additionl single unit mounted in-line or Two units, mounted Back to back, per Add-on Kit.

Rack Frame: 1.5 inch square tube 14 gauge hot rolled steel.

ACCESSORIES

Venting System: Exhaust manifold shall be a minimum of 3”, of either polypropylene or schedule 40 PVC/CPVC with horizontal or vertical termination.

Provide common vent system allowing up to twelve (12) units to vent through 6” vent diameter in the same system.

Provide system capable of configuring vent intake and exhaust in different pressure planes.

Exhaust damper: provide common vent system with dampers that allows venting without check valves.

EXECUTION

Examination

Do not begin work until adjacent substrates have been properly prepared to receive work specified in this section.

Verify that locations of concealed reinforcements have been clearly marked for the installer.

Locate reinforcement points and clearly mark their locations if not already done.

Preparation

Clean surfaces prior to installation.

Protect all adjacent surfaces from possible damage during installation of units.

Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

Installation

Coordinate with plumbing piping, fuel piping, and related electrical work to achieve operating system.

Install in accordance with manufacturer’s current installation instructions, industry recognized best practices, and all code bodies having jurisdiction; do not install damaged products.

Test for proper operation and adjust until satisfactory results are obtained, including start-up and check out procedures as recommended by the manufacturer.

Protect adjacent finishes from damage during installation using manufacturer’s recommendations.

Cleaning and Protection

Clean and remove all grime or other soils using manufacturer’s recommended methods.

Damaged products must be repaired or replaced prior to substantial completion.

Protect installed products until completion of work specified in this section.

END OF SECTION